## Introduction
Estimate of Residential Heat Loss
Date: | 2015-05-13 | Room: | Living Room
Job Name: | Manchester NH | Inside Temp (IDT): | 68 | (recommended)
Address: |  | Outside Temp (ODT): | -3
|  | Temp Difference: | 71
Estimator:
Instructions for use of the Residential BTU Estimate Form To determine the amount of heat required to provide comfort in a room or a house, it is necessary to calculate the amount of heat being lost (in BTU/hr) when winter conditions outdoors are at the Outside Design Temperature, which is the normal coldest temperature for that area. Heat is transmitted through all surfaces that will be warm on the inside and cold on the outside. This includes walls, ceilings, floors, windows and doors. If a room on the other side of a wall or ceiling is to have normal heating, then that wall is not considered "cold." In addition to the outward transmission losses, the infiltration of cold air must be added. Transmission + Infiltration equals the total heat loss, which must be replaced by the heating equipment. This calculator is suitable for either an individual room or for an entire house. If several rooms are to be calculated, use an individual calculator for each room. Design Temperature The amount of heat lost is directly related to the Temperature Difference (TD) between the desired Indoor Design Temperature (IDT) and the Outside Design Temperature (ODT). It is usually desirable to maintain 70° inside the room when the outside temperature is at its normal low point. The ODT for each major city is determined by long-range weather readings, and is fixed by the engineering profession. Subtracting ODT from the usual 70° gives the temperature difference for that locality. Do not calculate TD when using this form, unless the desired Inside Design Temperature is other than 70°. The Heat Loss Factors listed in the Heat Loss Factors tab are based on 70° IDT and 0° ODT. In localities where the ODT is not 0°, the temperature difference will be either greater or smaller than 70°, and so will the calculated heat loss. Outdoor Design Temperatures for different cities can be found on the ODT by City tab, and conversion numbers for other ODT's are shown on the ODT Conversion Tab.

## Heat Loss Calculator
Windows and Outside Doors | [8 empty] | Gross Cold Wall (Including windows and doors)
Height | x | Width | x | Quantity | = | Total Sq. Ft. |  |  |  | Height | x | Length | = | Sq. Ft.
4.5 |  | 5 |  | 6 |  | 135 |  |  | Front | 8 |  | 24 |  | 192
4.5 |  | 6 |  | 1 |  | 27 |  |  | L. Side | 8 |  | 24 |  | 192
[6 empty] | 0 |  |  | R. Side | 8 |  | 24 |  | 192
[6 empty] | 0 |  |  | Rear |  |  |  |  | 0
|  |  |  | Total (A): |  | 162 |  |  |  | Gross Cold Wall: |  |  |  | 576
[12 empty] | Gross Wall: |  | 576
Cold Ceiling (Attic or Roof Above) | [11 empty] | Subtract (A): |  | 162
Length | x | Width | = | Sq. Ft. | [7 empty] | Net Wall (B): |  | 414
24 |  | 24 |  | 576
|  |  |  | 0 | [10 empty] | Calculations
|  |  |  | 0 | [10 empty] | (Factors found in "Heat Loss Factors" Tab at Bottom)
Total Cold Ceiling (C): |  |  |  | 576 | [11 empty] | Multiply |  | x | Factor | = | BTU per Hour
[15 empty] | (A) Window and Doors: | 162 | Sq. Ft. |  | 45.5 |  | 7371
Infiltration (Volume) | [14 empty] | (B) Net Wall: | 414 | Sq. Ft. |  | 5.6 |  | 2318.4
Length | x | Width | x | Height | = | Cubic Feet | [8 empty] | (C) Cold Ceiling | 576 | Sq. Ft. |  | 1.4 |  | 806.4
24 |  | 24 |  | 8 |  | 4608 | [8 empty] | (D) Infiltration | 4608 | Cub. Ft. |  | 1.25 |  | 5760
[6 empty] | 0 | [8 empty] | (E) Cold Floor | 576 | Sq. Ft. |  | 4.2 |  | 2419.2
[6 empty] | 0 | [8 empty] | and/or | [5 empty] | 0
|  |  | Total Volume (D): |  |  | 4608 | [8 empty] | (E) Cold Floor | 0 | Lin. Ft. |  |  |  | 0
[15 empty] | BTU per hour heat loss at 0o Outside Design Temperature: | [5 empty] | 18675
Cold Floor (Over Cold Basement/Crawl Space) | [14 empty] | Conversion Number for other Outside Design Temperature (see Outdoor Design Temp Conversion tab): |  |  |  |  | x | 0.95714
Length | x | Width | = | Sq. Ft. | [12 empty] | Adjusted BTU/hr: |  |  |  | 17874.6429
24 |  | 24 |  | 576
0
Total Cold Floor (E): |  |  |  | 576
OR
Floor on Concrete Slab (Cold Edge Only)
Length | + | Width | + | Length | + | Width | = | Lin. Ft.
0
0
|  |  |  | Linear Ft. Total Cold Floor (E): |  |  |  | 0
Approximate Estimate of BTU/hr Residential Heat Loss* For Locations with 0° ODT For Other ODT's, use Conversion Numbers from ODT Conversion Tab Step 1: To determine transmission losses, Step 3: Select factors for each category measure all surfaces which will be of heat loss - A,B,C,D,E warm inside and cold outside. Step 4: Multiply each total below by the Step 2: To determine infiltration, calculate appropriate factor, and add all total volume of heated space. totals for the Total BTU/hr. *For exact calculations use the I=B=R method.
Heating Tips Boiler Selection: If installing a water boiler, its Net I=B=R Rating (in BTU/hr) should be equal to or slightly more than, the calculated BTU/hr heat loss. If the house will be used intermittently during winter, add 20% to the heat loss total for quick pick-up. Radiation Replacement: If modernizing an existing radiation system, certain cautions must be observed. Cast-iron radiation and copper-tube radiation have different response times, so they should not be mixed on the same circuit. Where both types exist in the house, they should be kept on separate zones. When adding radiation on a circuit or zone where existing radiation is excessively oversized, the new radiation should also be approximately oversized, to maintain a reasonable balance of heating output. Garage: If the garage will be unheated, walls of adjoining rooms and the floor above the garage should be considered "cold." By installing finned radiation about 50% of normal requirements, the adjoining room, the room above, and the cars in the garage will all benefit. Bathrooms: For bathrooms with tub or shower, add 20% to the calculated heat loss.

## Heat Loss Factors
Approximate Heat Loss Factors for Residential Construction
Factors per Square Foot for 70o Temperature Difference
(A) Glass and Outside Doors | Single | 80 |  | (D) Air Infiltration Faxtors x Cub. Ft. (For Indidual Room or Total House) | Fully Detached House | Assumed Air Changes | Factor | Attached House
| Double Glass | 45.5 |  |  | Very tight house, heavy insulation | 3/4 per hr. | 1 | Front and back exposed; insulated
| Storm Windows | 39.2 |  |  | Standard mondern house, some insulation | 1 per hr. | 1.25 | Front, back and 1 side exposed; insulated
(B) Walls (Not Insulated) | Wood Frame | 17.5 |  |  | Older house, good condition | 1-1/2 per hr. | 1.9 | Front, back and 1 side exposed; no insulation
| Brick | 22 |  |  | Loose construction, air leaks | 2 per hr. | 2.5
(B) Walls (Insulated) | 2" batts (R-7) | 7
| 3-5/8" batts (R-11) | 5.6
| 6" batts (R-19) | 4.2
(C) Cold Ceiling | Uninsulated | 21
| 2" batts (R-7) | 7.7
| 3-5/8" batts (R-11) | 4.9
| 6" batts (R-19) | 3.5
| 8" batts (R-28) | 2.1
| 12" batts (R-40) | 1.4
(E) Floor Over Unheated Basement | Uninsulated | 10.5
| 2" batts | 3.5
| 3-5/8" batts | 2.8
(E) Floor Over Cold Vented Crawl Space | Uninsulated | 25
| 2" batts | 6.2
| 3-5/8" batts | 4.2
Slab Floor on Grade (x Lin. Ft. Perimeter) | No Edge Insulation | 60
| 1" Edge Insulation | 48.3
| 2" Edge Insulation | 37.1
Heated (finished) Basement Room Factors | Floor (sq. ft.) | 2.8
| Foundation Wall (Uninsulated) | Above Grade | 37
|  | Below Grade | 4.2
| Foundation Wall (2" Insulation) | Above Grade | 9
|  | Below Grade | 3

## ODT by City
UNITED STATES |  | CANADA
ALABAMA | ODT | ALBERTA | ODT
Alexander City | 22 | Calgary AP | -23
Anniston AP | 22 | Edmonton AP | -25
Auburn | 22 | Grande Prairie AP | -33
Birmingham AP | 21 | Jasper | -26
Decatur | 16 | Lethbridge AP | -22
Dothan AP | 27 | McMurray AP | -38
Florence AP | 21 | Medicine Hat AP | -24
Gadsden | 20 | Red Deer AP | -26
Huntsville AP | 16
Mobile AP | 29 | BRITISH COLUMBIA | ODT
Mobile CO | 29 | Dawson Creek | -33
Selma, Craig AFB | 25 | Fort Nelson AP | -40
Montgomery AP | 26 | Kamloops CO | -15
Talladega | 22 | Nanaimo | 20
Tuscaloosa AP | 23 | New Westminister | 18
|  | Penticton AP | 4
ALASKA | ODT | Prince George AP | -28
Anchorage AP | -18 | Prince Rupert CO | 2
Barrow | -41 | Trail | 0
Fairbanks AP | -47 | Vancouver AP | 19
Juneau AP | 1 | Victoria CO | 23
Kodiak | 12
Nome AP | -27 | MANITOBA | ODT
|  | Brandon | -27
ARIZONA | ODT | Churchill AP | -39
Douglas AP | 31 | Dauphin AP | -28
Flagstaff AP | 4 | Flin Flon | -37
Fort Huachuca AP | 28 | Portage La Prairie AP | -24
Kingman AP | 25 | The Pas AP | -33
Nogales | 32 | Winnipeg AP | -27
Phoenix AP | 34
Prescott AP | 9 | NEW BRUNSWICK | ODT
Tucson AP | 32 | Campbellton CO | -14
WinslowAP | 10 | Chatham AP | -10
Yuma AP | 39 | Edmundston CO | -16
|  | Fredericton AP | -11
ARKANSAS | ODT | Moncton AP | -8
Blytheville AFB | 15 | Saint John AP | -8
Camden | 23
EI Dorado AP | 23 | NEWFOUNDLAND | ODT
Fayetteville AP | 12 | Corner Brook | 0
Fort Smith AP | 17 | Gander AP | -1
Hot Springs | 23 | Goose Bay AP | -24
Jonesboro | 15 | St. John's AP | 7
Little Rock AP | 20 | Stephenville AP | 4
Pine Bluff AP | 22
Texarkana AP | 23 | NORTHWEST TERRITORIES | ODT
|  | Fort Smith AP | -45
CALIFORNIA | ODT | Frobisher AP | -41
Bakersfield AP | 32 | Inuvik | -53
Blythe AP | 33 | Resolute AP | -47
Burbank AP | 39 | Yellowknife AP | -46
Chico | 30
Concord | 27 | NOVA SCOTIA | ODT
Covina | 35 | Amherst | -6
Crescent City AP | 33 | Halifax AP | 5
Downey | 40 | Kentville | 1
EI Cajon | 44 | New Glasgow | -5
EI Centro AP | 38 | Sydney AP | 3
Escondido | 41 | Truro CO | -5
Eureaka/Arcata AP | 33 | Yarmouth AP | 9
Fairfield-Travis AFB | 32
Fresno AP | 30 | ONTARIO | ODT
Hamilton AFB | 32 | Belleville | -7
Laguna Beach | 43 | Chatham | 3
Livermore | 27 | Cornwall | -9
Lompoc, Vandenburg AFB | 38 | Hamilton | 1
Long Beach AP | 43 | Kaupuskasing AP | -28
Los Angeles AP | 43 | Kenora AP | -28
Los Angeles CO | 40 | Kingston | -7
Merced-CastleAFB | 31 | Kitchener | -2
Modesto | 30 | London AP | 0
Monterey | 38 | North Bay AP | -18
Napa | 32 | Oshawa | -3
Needles AP | 33 | Ottawa AP | -13
Oakland AP | 36 | Owen Sound | -2
Oceanside | 43 | Peterborough | -9
Ontario | 33 | St. Catharines | 3
Oxnard | 36 | Sarnia | 3
Palmdale AP | 22 | Sault Ste. Marie AP | -13
Palm Springs | 35 | Sudbury AP | -19
Pasadena | 35 | Thunder Bay AP | -24
Petaluma | 29 | Timmins AP | -29
Pomona CO | 30 | Toronto AP | -1
Redding AP | 31 | Windsor AP | 4
Redlands | 33
Richmond | 36 | PRINCE EDWARD ISLAND | ODT
Riverside-March AFB | 32 | Charlottetown AP | -4
Sacramento AP | 32 | Summerside AP | -4
Salinas AP | 32
San Bernadino, Norton AFB | 33 | QUEBEC | ODT
San Diego AP | 44 | Bagotville AP | -23
San Fernando | 39 | Chicoutimi | -22
San Francisco AP | 38 | Drummondville | -14
San Francisco CO | 40 | Granby | -14
San Jose AP | 36 | Hull | -14
San Luis Obispo | 35 | Megantic AP | -16
Santa Ana AP | 39 | Montreal AP | -10
Santa Barbara MAP | 36 | Quebec AP | -14
Santa Cruz | 38 | Rimouski | -12
Santa Maria AP | 33 | St. Jean | -11
Santa Monica CO | 43 | St. Jeirome | -13
Santa Paula | 35 | Sept. lies AP | -21
Santa Rosa | 29 | Shawinigan | -14
Stockton AP | 30 | Sherbrooke CO | -21
Ukiah | 29 | Thetford Mines | -14
Visalia | 30 | Trois Rivieres | -13
Yreka | 17 | Val d'Or AP | -27
Yuba City | 31 | Valleyfield | -10
COLORADO | ODT | SASKATCHEWAN | ODT
Alamosa AP | -6 | Estevan AP | -25
Boulder | 0 | Moose Jaw AP | -25
Colorado Springs AP | 2 | North Battleford AP | -30
Denver AP | 1 | Prince Albert AP | -35
Durango | -1 | Regina AP | -29
Fort Collins | 1 | Saskatoon AP | -31
Grand Junction AP | 7 | Swift Current AP | -25
Greeley | 4 | Yorkton AP | -30
LaJunta AP | 3
Leadville | -14 | YUKON TERRITORY | ODT
Puebio AP | 0 | Whitehorse AP | -43
Sterling | -2
Trinidad AP | 3
CONNECTICUT | ODT
Bridgeport AP | 9
Hartford, Brainard Field | 7
New Haven AP | 7
New London | 9
Norwalk. | 9
Norwich | 7
Waterbury | 2
.Windsor L.ocks, Bradley Field | 4
DELAWARE | ODT
Dover AFB | 15
Wilmington AP | 14
DISTRICT OF COLUMBIA | ODT
Andrews AFB | 14
Washington National AP | 17
FLORIDA | ODT
Belle Glade | 44
Cape Kennedy AP | 38
Daytona Beach AP | 35
Fort L.auderdale | 46
Fort Myers Ap | 44
Fort Pierce | 42
Gainesville AP | 31
Jacksonville AP | 32
Key WestAP | 57
Lakeland CO | 41
MiamiAP | 47
Miami Beach CO | 48
Ocala | 34
Orlando AP | 38
Panama City, Tyndall AFB | 33
Pensacola CO | 29
St. Augustine | 35
St. Petersburg | 40
Sanford | 38
Sarasota | 42
Tallahassee AP | 30
Tampa AP | 40
West Palm Beach AP | 45
GEORGIA | ODT
Albany, Turner AFB | 29
Americus | 25
Athens | 22
Atlanta AP | 22
Augusta AP | 23
Brunswick | 32
Columbus, Lawson AFB | 24
Dalton | 22
Dublin | 25
Gainesville | 21
Griffin | 22
La Grange | 23
MaconAP | 25
Marietta, Dobbins AFB | 21
Moultrie | 30
Rome AP | 22
Savannah-Travis AP | 27
Valdosta-Moody AFB | 31
Waycross | 29
HAWAII | ODT
Hilo AP | 62
Honolulu AP | 63
Kaneohe Bay MCAS | 66
Wahalwa | 59
IDAHO | ODT
BoiseAP | 10
Burley | 2
Coeur D'Alene AP | -1
Idaho Falls AP | -6
Lewiston AP | 6
Moscow | 0
Mountain Home AFB | 12
Pocatello AP | -1
Twin Falls AP | 2
ILLINOIS | ODT
Aurora | -1
Belleville, Scott AFT | 6
Bloomington | -2
Carbondale | 7
Champaign/Urbana | 2
Chicago, Midway AP | 0
Chicago, O'Hare AP | -4
Chicago CO | 2
Danville | 1
47 Decatur | 2
Dixon | -2
Elgin | -2
Freeport | -4
Galesburg | -2
Greenville | 4
Joliet | 0
Kankakee | 1
LaSalle/Peru | -2
Macomb | 0
Moline AP | -4
Mt. Vernon | 5
Peoria AP | -4
Quincy AP | 3
Rantoul, Chanute AFB | 1
Rockford | -4
Springfield AP | 2
Waukegan | -3
INDIANA | ODT
Anderson | 6
Bedford | 5
Bloomington | 5
Columbus, Bakalar AFB | 7
Crawfordsville | 3
Evansville AP | 9
Fort Wayne AP | 1
Goshen AP | 1
Hobart | 2
Huntington | 1
Indianapolis AP | 2
Jeffersonville | 10
Kokomo | 0
Layfayette | 3
LaPorte | 3
Marion | 0
Muncie | 2
Peru, Bunker Hill AFB | -1
Richmond AP | 2
Shelbyville | 3
South Bend AP | 1
Terre Haute AP | 4
Valparaise | 3
Vincennes | 6
IOWA | ODT
Ames | -6
Burlington AP | -3
Cedar Rapids AP | -5
Clinton | -3
Council Bluffs | -3
Des Moines AP | -5
Debuque | -7
Fort Dodge | -7
Iowa City | -6
Keokuk | 0
Marshalltown | -7
Mason City AP | -11
Newton | -5
Ottumwa AP | -4
Sioux City Ap | -7
Waterloo | -10
KANSAS | ODT
Atchison | 2
Chanute AP | 7
Dodge City AP | 5
EI Dorado | 7
Emporia | 5
Garden City AP | 4
Goodland AP | 0
Great Bend | 4
Hutchinson AP | 8
Liberal | 7
Manhattan, Fort Riley | 3
Parsons | 9
Russel AP | 4
Salina | 5
Topeka AP | 4
Parsons | 9
KENTUCKY | ODT
Ashland | 10
Bowling Green AP | 10
Corbin AP | 9
Covington AP | 6
Hopkinsville, Campbell AFB | 10
Lexington AP | 8
Louisville AP | 10
Madisonville | 10
Owensboro | 10
Paducah | 12
LOUISIANA | ODT
Alexandria AP | 27
Baton Rouge AP | 29
Bogalusa | 28
Houma | 35
Lafayette AP | 30
Lake Charles AP | 31
Minden | 25
Monroe AP | 25
Natchitoches | 26
New Orleans AP | 33
Shreveport AP | 25
MAINE | ODT
Augusta AP | -3
Bangor, Dow AFB | -6
Caribou | -13
Lewiston | -2
Millinocket AP | -9
Portland | -1
Waterville | -4
MARYLAND | ODT
Baltimore AP | 13
Baltimore CO | 17
Cumberland | 10
Frederick AP | 12
Hagerstown | 12
Salisbury | 16
MASSACHUSETTS | ODT
Boston AP | 9
Clinton | 2
Fall River | 9
Framingham | 6
Gloucester | 5
Greenfield | -2
Lawrence | 0
Lowell | 1
New Bedford | 9
Pittsfield AP | -3
Springfield, Westover AFB | 0
Tauton | 9
Worcester AP | 4
MICHIGAN | ODT
Adrian | 3
Alpena AP | -6
Battle Creek AP | 5
Benton Harbor AP | 5
Detroid | 6
Escanaba | -7
Flint AP | 1
Grand Rapids | 5
Holland | 6
Jackson AP | 5
Kalamazoo | 5
Lansing AP | 1
Marquette CO | -8
Mt. Pleasant | 4
MuskegonAP | 6
Pontiac | 4
Port Huron | 4
Saginaw AP | 4
Sault Ste. Marie AP | -8
Traverse City AP | 1
Yipsilanti | 5
MINNESOTA | ODT
Albert Lea | -12
Alexandria AP | -16
Bemidji AP | -26
Brainerd | -16
Duluth AP | -16
Fairbault | -12
Fergus Falls | -17
International Falls AP | -25
Mankato | -12
Mil1neapolis/St. Paul AP | -12
Rochester AP | -12
St. Cloud AP | -11
Virginia | -21
Wilmar | -11
Winona | -10
MISSISSIPPI | ODT
Biloxi, Keesler AFB | 31
Clarksdale | 19
Columbus AFB | 20
Greenville AFB | 20
Greenwood | 20
Hattiesburg | 27
Jackson AP | 25
Laurel | 27
McComb AP | 26
Meridian AP | 23
Natchez | 27
Tupelo | 19
Vicksburg CO | 26
MISSOURI | ODT
Cape Girardeau | 13
Columbia AP | 4
Farmington AP | 8
Hannibal | 3
Jefferson City | 7
Joplin AP | 10
Kansas City AP | 6
Kirksville AP | 0
Mexico | 4
Moberly | 3
Poplar Bluff | 16
Rolla | 9
St. Joseph AP | 2
St. Louis AP | 6
St. Louis CO | 8
Sedalia, Whiteman AFB | 4
Sikeston | 15
Springfield AP | 9
MONTANA | ODT
Billings AP | -10
Bozeman | -14
Butte AP | -17
Cut BankAP | -20
Glasgow AP | -18
Glasgow AP | -18
Glenclive | -13
Great Falls AP | -15
Havre | -11
Helena AP | -16
Kalispell AP | -7
Lewiston AP | -16
Livingston AP | -14
NEBRASKA | ODT
Beatrice | -2
Chadron AP | -3
Columbus | -2
Fremont | -2
Grand Island AP | -3
Hastings | -3
Kearney | -4
Lincoln CO | -2
McCook | -2
Norfolk | -4
North Platte AP | -4
Omaha AP | -3
Scottsbluff AP | -3
Sidney AP | -3
NEVADA | ODT
Carson City | 9
Elko AP | -2
Ely AP | -4
Las Vegas AP | 28
Lovelock AP | 12
Reno AP | 10
Reno CO | 11
Tonapah AP | 10
Winnemucca AP | 3
NEW HAMPSHIRE | ODT
Berlin | -9
Claremont | -4
Concord AP | -3
Keene | -7
Laconia | -5
Manchester, Grenier AFB | -3
Portsmouth, Pease AFM | 2
NEW JERSEY | ODT
Atlantic City CO | 13
Long Branch | 13
Newark AP | 14
New Brunswick | 10
Patterson | 10
Phillipsburg | 6
Trenton CO | 14
Vineland | 11
NEW MEXICO | ODT
Alamagordo, Holloman AFB | 19
Albuquerque AP | 16
Artesia | 19
Carlsbad AP | 19
Clovis AP | 13
Farmington AP | 6
Gallup | 5
Grants | 4
Hobbs AP | 18
Las Cruces | 20
Los Alamos | 9
Raton AP | 1
Roswell, Walker AFB | 18
Santa Fe CO | 10
Silver City AP | 10
Socorro AP | 17
Tucumcari AP | 13
NEW YORK | ODT
Albany AP | -1
Albany CO | 1
Auburn | 2
Batavia | 5
Binghamton AP | 1
Buffalo AP | 6
Cortland | 0
Dunkirk | 9
Elmira AP | 1
Geneva | 2
Glen Falls | -5
Gloversville | -2
Hornell | 0
Ithaca | 0
Jamestown | 3
Kingston | 2
Lockport | 7
Massena AP | -8
Newburg-Stewart AFB | 4
NYC - Central Park | 15
NYC - Kennedy AP | 15
NYC - La Guardia AP | 15
Niagra Falls ANYC LaP | 7
Olean | 2
Oneonta | -4
Oswego CO | 7
Plattsburg AFB | -8
Poughkeepsie | 6
Rochester AP | 5
Rome-Griffiss AFB | -5
Schenectady | 1
Suffolk County AFB | 10
Syracuse AP | 2
Utica | -6
Watertown | -6
NORTH CAROLINA | ODT
Ashville AP | 14
Charlotte AP | 22
Durham | 20
Elizabeth City AP | 19
Fayetteville, Pope AFB | 20
Goldsboro, Seymour-Johnson AFB | 21
Greensboro AP | 18
Greenville | 21
Henderson | 15
Hickory | 18
Jacksonville | 24
Lumberton | 21
New Bern AP | 24
Raleigh/Durham AP | 20
Rocky Mount | 21
Wilmington AP | 26
Winston-Salem AP | 20
NORTH DAKOTA | ODT
Bismark AP | -19
Devil's Lake | -21
Dickinson AP | -17
Fargo AP | -18
Grands Forks AP | -22
Jamestown AP | -18
Minot AP | -20
Williston | -21
OHIO | ODT
Akron-Canton AP | 6
Ashtabula | 9
Athens | 6
Bowling Green | 2
Cambridge | 7
Chilicothe | 6
Cincinnati CO | 6
Cleveland AP | 5
Columbus AP | 5
Dayton AP | 4
Defiance | 4
Findlay AP | 3
Fremont | 1
Hamilton | 5
Lancaster | 5
Lima | 4
Mansfield AP | 5
Marion | 5
Middleton | 5
Newark | 5
Norwalk | 1
Portsmouth | 10
Sandusky CO | 6
Springfield | 3
Stubenville | 5
Toledo AP | 1
Warren | 5
Wooster | 6
Youngstown AP | 4
Zanesville AP | 7
OKLAHOMA | ODT
Ada | 14
Altus AFB | 16
Ardmore | 17
Bartlesville | 10
Chickasha | 14
Enid-Vance AFB | 13
Lawton AP | 16
McAlester | 19
Muskogee AP | 15
Norman | 13
Oklahoma City AP | 13
Ponca City | 9
Seminole | 15
Stillwater | 13
Tulsa AP | 13
Woodward | 10
OREGON | ODT
Albany | 22
Astoria AP | 29
Baker AP | 6
Bend | 4
Corvallis | 22
Eugene AP | 22
Grants Pass | 24
Klamath Falls AP | 9
Medford AP | 23
Pendleton AP | 5
Portland AP | 23
Portland CO | 24
Roseburg AP | 23
Salem AP | 23
The Dallas | 19
PENNSYLVANIA | ODT
Allentown AP | 9
Altoona CO | 5
Butler | 6
Chambersburg | 8
Erie AP | 9
Harrisburg AP | 11
Johnstown | 2
Lancaster | 8
Meadville | 4
New Castle | 7
Philadelphia AP | 14
Pittsburgh AP | 5
Pittsburgh CO | 7
Reading CO | 13
Scranton/Wilkes-Barre | 5
State College | 7
Sunbury | 7
Uniontown | 9
Warren | 4
West Chester | 13
Williamsport AP | 7
York | 12
RHODE ISLAND | ODT
Newport | 9
Providence AP | 9
SOUTH CAROLINA | ODT
Anderson | 23
Charleston AFB | 27
Charleston CO | 28
Columbia AP | 24
Florence AP | 25
Georgetown | 26
Greenville AP | 22
Greenwood | 22
Orangeburg | 24
Rock Hill | 23
Spartanburg AP | 22
Sumter-Shaw AFB | 25
SOUTH DAKOTA | ODT
Aberdeen AP | -15
Brookings | -13
Huron AP | -14
Mitchel | -10
Pierre AP | -10
Rapid City AP | -7
Sioux Falls AP | -11
Watertown AP | -15
Yankton | -7
TENNESSEE | ODT
Athens | 18
Bristol-Tri City AP | 14
Chattanooga AP | 18
Clarksville | 12
Columbia | 15
Dyersburg | 15
Greenville | 16
Jackson AP | 16
Knoxville AP | 19
Memphis AP | 18
Murfreesboro | 14
Nashville AP | 14
Tullahoma | 13
TEXAS | ODT
Abilene AP | 20
Alice AP | 34
Amarillo AP | 11
Austin AP | 28
Bay City | 33
Beaumont | 31
Beeville | 33
Big Springs AP | 20
Brownsville AP | 39
Brownwood | 22
Bryan AP | 29
Corpus Christi AP | 35
Corsicana | 25
Dallas AP | 22
Del Rio, Laughlin AFB | 31
Denton | 22
Eagle Pass | 32
EI Paso AP | 24
Fort Worth AP | 22
Galveston AP | 36
Greenville | 22
Harlingen | 39
Houston AP | 32
Houston CO | 33
Huntsville | 27
Killeen-Gray AFB | 25
Lamesa | 17
Laredo AFB | 36
Longview | 24
LubbockAP | 15
Lufkin AP | 29
McAllen | 39
Midland AP | 21
Palestine CO | 27
Pampa | 12
Pecos | 21
Plainview | 13
Port Arthur AP | 31
San Angelo, Goodfellow AFB | 22
San Antonio AP | 30
Sherman-Perrin AFB | 20
Snyder | 18
Temple | 27
Tyler AP | 24
Vemon | 17
Victoria AP | 32
WacoAP | 26
Wichita Falls AP | 18
UTAH | ODT
Cedar City AP | 5
Logan | 2
Moab | 11
Ogden AP | 5
Price | 5
Provo | 6
Richfield | 5
St. George CO | 21
Salt Lake City AP | 8
Vernal AP | 0
VERMONT | ODT
Barre | -11
Burlington AP | -7
Rutland | -8
VIRGINIA | ODT
Charlottesville | 18
Danville AP | 16
Fredericksburg | 14
Harrisonburg | 16
Lynchburg AP | 16
Norfolk AP | 22
Petersburg | 17
Richmond AP | 17
Roanoke AP | 16
Staunton | 16
Winchester | 10
WASHINGTON | ODT
Aberdeen | 28
Bellingham AP | 15
Bremerton | 25
Ellensburg AP | 6
Everett-pa.ine AFB | 25
Kennewick | 11
Longview | 24
Moses Lake, Larson AFB | 7
OlympiaAP | 22
Port Angeles | 27
Seattle-Boeing Fld | 26
Seattle CO | 27
Seattle-Tacoma AP | 26
Spokane AP | 2
Tacoma-McChord AFB | 24
Walla Walla AP | 7
Wenatchee | 11
Yakima AP | 5
WEST VIRGINIA | ODT
Beckley | 4
Bluefield AP | 4
Charleston AP | 11
Clarksburg | 10
Elkins AP | 6
Huntington CO | 10
Martinsburg AP | 10
Morgantown AP | 8
Parkersburg CO | 11
Wheeling | 5
WISCONSIN | ODT
Appleton | -9
Ashland | -16
Beloit | -3
Eau Claire AP | -11
Fond du Lac | -8
Green Bay AP | -9
LaCrosse AP | -9
Madison AP | -7
Manitowoc | -7
Marinette | -11
Milwaukee AP | -4
Racine | -2
Sheboygan | -6
Stevens Point | -11
Waukesha | -5
Wausau AP | -12
WYOMING
Casper AP | -5
Cheyene AP | -1
Cody AP | -13
Evanston | -3
Lander AP | -11
Laramie AP | -6
Newcastle | -12
Rawlins | -4
Rock Springs AP | -3
Sheridan AP | -8
Torrington | -8

## ODT Conversion
For other Outside Design Temperature, Multiply Total BTU/hr. by Conversion Number
Ouside Temperature | -20° | -15° | -10° | -5° | 0° | +5° | +10° | +15° | +20°
Conversion Number | 1.29 | 1.21 | 1.14 | 1.07 | 1 | 0.93 | 0.86 | 0.79 | 0.71
0.95714
To get the Conversion Number for Outdoor Design Temperatures not listed above, calculate the Temperature Difference (IDT minus ODT) and divide by 70. Examples: 70 IDT - (+30) = 40 ÷ 70 = .57 70 IDT - (-30) = 100 ÷ 70 = 1.43