## main
TYPE | START DATE | END DATE | USAGE | Units | Adj. usage | COST | days | HDD | units/HDD | BTUs/unit | BTU/HDD_input | BTU/HDD_output | COP | Equipment in use
Gas bill | 2021-10-15 | 2021-11-12 | 43 | Therms | 43 | 84.16 | 28 | 461.7 | 0.093134 | 99976.1 | 9311.1811 | 8659.3984 | 0.93 | Gas furnace
Gas bill | 2021-11-13 | 2021-12-13 | 95 | Therms | 95 | 173.73 | 30 | 871.1 | 0.10906 | 99976.1 | 10903.1449 | 10139.9247 | 0.93 | Gas furnace
Gas bill | 2021-12-14 | 2022-01-13 | 110 | Therms | 110 | 199.23 | 30 | 1023.1 | 0.10752 | 99976.1 | 10749.0675 | 9996.6328 | 0.93 | Gas furnace
Gas bill | 2022-01-14 | 2022-02-14 | 144 | Therms | 144 | 257.02 | 31 | 1301 | 0.11068 | 99976.1 | 11065.7636 | 10291.1601 | 0.93 | Gas furnace
Electric bill | 2022-10-22 | 2022-11-21 | 816 | kwh | 262.5116 | 331.33 | 30 | 547.2 | 0.47974 | 3412.14 | 1636.9268 | 10142.5726 | 6.1961 | ASHP
Electric bill | 2022-11-22 | 2022-12-21 | 1209 | kwh | 673.9612 | 575.87 | 29 | 907.2 | 0.7429 | 3412.14 | 2534.8876 | 10142.5726 | 4.0012 | ASHP and ERV
Electric bill | 2022-12-22 | 2023-01-23 | 1346 | kwh | 755.6124 | 641.35 | 32 | 1068.6 | 0.7071 | 3412.14 | 2412.7412 | 10142.5726 | 4.2038 | ASHP and ERV
Electric bill | 2023-01-24 | 2023-02-21 | 1412 | kwh | 895.4108 | 672.93 | 28 | 916.7 | 0.97678 | 3412.14 | 3332.8975 | 10142.5726 | 3.0432 | ASHP and ERV

## HDD_data
Description: | Fahrenheit-based heating degree days with a base temperature of 65 F
Source: | www.degreedays.net
Accuracy: | Estimates were made to account for missing data: the "% Estimated" column shows how much each figure was affected (0% is best, 100% is worst)
Station: | WESTFIELD BARNES MUNICIPAL, MA, US (72.72W,42.16N)
Station ID: | KBAF
Date | HDD 65 | % Estimated
2020-02-01 | 31.8 | 0
2020-02-02 | 30.9 | 0
2020-02-03 | 30.8 | 0
2020-02-04 | 27.8 | 0
2020-02-05 | 28.4 | 0
2020-02-06 | 33.8 | 0
2020-02-07 | 33 | 0
2020-02-08 | 39.2 | 2
2020-02-09 | 41.9 | 0
2020-02-10 | 29 | 0
2020-02-11 | 28.8 | 0
2020-02-12 | 27.6 | 0
2020-02-13 | 31 | 0
2020-02-14 | 43 | 0
2020-02-15 | 48.5 | 0
2020-02-16 | 33.7 | 0
2020-02-17 | 33.3 | 0
2020-02-18 | 34.6 | 0
2020-02-19 | 30.1 | 0
2020-02-20 | 40.1 | 0
2020-02-21 | 44.1 | 0
2020-02-22 | 36.3 | 0
2020-02-23 | 30.7 | 0
2020-02-24 | 24.1 | 0
2020-02-25 | 21.5 | 0
2020-02-26 | 22 | 0
2020-02-27 | 27 | 0
2020-02-28 | 33.8 | 1
2020-02-29 | 41.3 | 0
2020-03-01 | 39.4 | 0
2020-03-02 | 24.3 | 0
2020-03-03 | 16.2 | 0
2020-03-04 | 19.6 | 0
2020-03-05 | 25.4 | 0
2020-03-06 | 28.4 | 0
2020-03-07 | 29.1 | 0
2020-03-08 | 22.9 | 0
2020-03-09 | 14.9 | 0
2020-03-10 | 8.5 | 0
2020-03-11 | 19.9 | 0
2020-03-12 | 24.2 | 0
2020-03-13 | 20.1 | 0
2020-03-14 | 23 | 0
2020-03-15 | 24.4 | 0
2020-03-16 | 32.6 | 0
2020-03-17 | 27.5 | 0
2020-03-18 | 20.3 | 0
2020-03-19 | 24.7 | 0
2020-03-20 | 14.3 | 0
2020-03-21 | 23.4 | 0
2020-03-22 | 33.1 | 0
2020-03-23 | 33.2 | 0
2020-03-24 | 26.9 | 0
2020-03-25 | 29 | 0
2020-03-26 | 22.4 | 0
2020-03-27 | 12.5 | 0
2020-03-28 | 25.1 | 0
2020-03-29 | 22 | 0
2020-03-30 | 25 | 0
2020-03-31 | 25.6 | 0
2020-04-01 | 23.3 | 0
2020-04-02 | 21.2 | 0
2020-04-03 | 19.4 | 0
2020-04-04 | 15.8 | 0
2020-04-05 | 14.2 | 0
2020-04-06 | 14.4 | 0
2020-04-07 | 12.4 | 0
2020-04-08 | 15.5 | 0
2020-04-09 | 20.9 | 0
2020-04-10 | 23.1 | 0
2020-04-11 | 22.5 | 0
2020-04-12 | 19.1 | 0
2020-04-13 | 8.8 | 0
2020-04-14 | 15.5 | 0
2020-04-15 | 21.8 | 0
2020-04-16 | 27 | 0
2020-04-17 | 25.4 | 0
2020-04-18 | 29.5 | 0
2020-04-19 | 19.5 | 0
2020-04-20 | 18.4 | 0
2020-04-21 | 24.9 | 0
2020-04-22 | 27.4 | 0
2020-04-23 | 24 | 0
2020-04-24 | 23 | 0
2020-04-25 | 15.3 | 0
2020-04-26 | 20.2 | 0
2020-04-27 | 24.9 | 0
2020-04-28 | 16.6 | 0
2020-04-29 | 16.8 | 0
2020-04-30 | 17.4 | 0
2020-05-01 | 8.1 | 0
2020-05-02 | 7.4 | 0
2020-05-03 | 4.3 | 0
2020-05-04 | 6.8 | 0
2020-05-05 | 15.3 | 1
2020-05-06 | 18.1 | 0
2020-05-07 | 12 | 0
2020-05-08 | 17.4 | 0
2020-05-09 | 26.6 | 0
2020-05-10 | 17.4 | 0
2020-05-11 | 19.2 | 0
2020-05-12 | 18.7 | 0
2020-05-13 | 17.3 | 0
2020-05-14 | 11.4 | 0
2020-05-15 | 5.1 | 0
2020-05-16 | 2 | 0
2020-05-17 | 5.5 | 0
2020-05-18 | 7.7 | 0
2020-05-19 | 8.5 | 0
2020-05-20 | 9.3 | 0
2020-05-21 | 9.8 | 0
2020-05-22 | 4.8 | 0
2020-05-23 | 1.7 | 0
2020-05-24 | 7.8 | 0
2020-05-25 | 6.4 | 0
2020-05-26 | 1.4 | 0
2020-05-27 | 1.3 | 0
2020-05-28 | 0.4 | 0
2020-05-29 | 0 | 0
2020-05-30 | 0.1 | 0
2020-05-31 | 6.9 | 0
2020-06-01 | 13.1 | 0
2020-06-02 | 10.1 | 0
2020-06-03 | 3.4 | 0
2020-06-04 | 0.3 | 0
2020-06-05 | 0 | 0
2020-06-06 | 0 | 0
2020-06-07 | 3.8 | 0
2020-06-08 | 6.2 | 0
2020-06-09 | 2 | 0
2020-06-10 | 0.8 | 0
2020-06-11 | 0 | 0
2020-06-12 | 0.3 | 0
2020-06-13 | 4.7 | 0
2020-06-14 | 7.1 | 0
2020-06-15 | 4.1 | 0
2020-06-16 | 5.1 | 0
2020-06-17 | 4.1 | 0
2020-06-18 | 1.1 | 0
2020-06-19 | 0 | 0
2020-06-20 | 0.1 | 0
2020-06-21 | 0.1 | 0
2020-06-22 | 0 | 0
2020-06-23 | 0 | 0
2020-06-24 | 0.1 | 0
2020-06-25 | 1.9 | 0
2020-06-26 | 1.4 | 0
2020-06-27 | 1.8 | 0
2020-06-28 | 1.1 | 0
2020-06-29 | 0.2 | 0
2020-06-30 | 0.1 | 0
2020-07-01 | 0.5 | 0
2020-07-02 | 1.3 | 0
2020-07-03 | 0 | 0
2020-07-04 | 0.6 | 0
2020-07-05 | 0 | 0
2020-07-06 | 0.1 | 0
2020-07-07 | 0.2 | 0
2020-07-08 | 0 | 0
2020-07-09 | 0 | 0
2020-07-10 | 0 | 0
2020-07-11 | 0 | 0
2020-07-12 | 0 | 0
2020-07-13 | 0 | 0
2020-07-14 | 0.1 | 0
2020-07-15 | 0 | 0
2020-07-16 | 0 | 0
2020-07-17 | 1 | 0
2020-07-18 | 0.4 | 0
2020-07-19 | 0.1 | 0
2020-07-20 | 0 | 0
2020-07-21 | 0.1 | 0
2020-07-22 | 0 | 0
2020-07-23 | 0 | 0
2020-07-24 | 0 | 0
2020-07-25 | 0.1 | 0
2020-07-26 | 0 | 0
2020-07-27 | 0 | 0
2020-07-28 | 0 | 0
2020-07-29 | 0.8 | 0
2020-07-30 | 0 | 0
2020-07-31 | 0 | 0
2020-08-01 | 0.2 | 0
2020-08-02 | 0 | 0
2020-08-03 | 0 | 0
2020-08-04 | 0 | 4
2020-08-05 | 0 | 0
2020-08-06 | 1.5 | 0
2020-08-07 | 0.5 | 0
2020-08-08 | 0 | 0
2020-08-09 | 0 | 0
2020-08-10 | 0 | 0
2020-08-11 | 0 | 0
2020-08-12 | 0 | 0
2020-08-13 | 0 | 0
2020-08-14 | 0.6 | 0
2020-08-15 | 0.5 | 0
2020-08-16 | 0.1 | 0
2020-08-17 | 0.6 | 0
2020-08-18 | 0.4 | 0
2020-08-19 | 3.6 | 0
2020-08-20 | 4.1 | 0
2020-08-21 | 3.6 | 0
2020-08-22 | 0.7 | 0
2020-08-23 | 0.6 | 0
2020-08-24 | 0 | 0
2020-08-25 | 0 | 0
2020-08-26 | 2 | 0
2020-08-27 | 3.4 | 0
2020-08-28 | 1.4 | 0
2020-08-29 | 0.9 | 0
2020-08-30 | 1.5 | 0
2020-08-31 | 6 | 0
2020-09-01 | 2.9 | 0
2020-09-02 | 1.3 | 0
2020-09-03 | 0 | 0
2020-09-04 | 1.8 | 0
2020-09-05 | 5.5 | 0
2020-09-06 | 3 | 0
2020-09-07 | 2.7 | 0
2020-09-08 | 1.1 | 0
2020-09-09 | 0.1 | 0
2020-09-10 | 0 | 0
2020-09-11 | 1.3 | 0
2020-09-12 | 7.2 | 0
2020-09-13 | 5.2 | 0
2020-09-14 | 1.9 | 0
2020-09-15 | 13.4 | 0
2020-09-16 | 9 | 0
2020-09-17 | 4.9 | 0
2020-09-18 | 6.5 | 0
2020-09-19 | 16.3 | 0
2020-09-20 | 17.2 | 0
2020-09-21 | 17.6 | 0
2020-09-22 | 14 | 0
2020-09-23 | 4.2 | 0
2020-09-24 | 5.3 | 0
2020-09-25 | 5.2 | 0
2020-09-26 | 2.5 | 0
2020-09-27 | 0 | 0
2020-09-28 | 0 | 0
2020-09-29 | 0 | 0
2020-09-30 | 2.8 | 0
2020-10-01 | 8.1 | 0
2020-10-02 | 11 | 0
2020-10-03 | 14.1 | 0
2020-10-04 | 15.9 | 0
2020-10-05 | 10.3 | 0
2020-10-06 | 8.6 | 0
2020-10-07 | 7 | 1
2020-10-08 | 11 | 0
2020-10-09 | 15 | 0
2020-10-10 | 4.3 | 0
2020-10-11 | 7.6 | 0
2020-10-12 | 16.3 | 0
2020-10-13 | 15 | 0
2020-10-14 | 12.2 | 0
2020-10-15 | 10.6 | 0
2020-10-16 | 8.9 | 0
2020-10-17 | 18.1 | 0
2020-10-18 | 21.1 | 0
2020-10-19 | 16.3 | 1
2020-10-20 | 6.2 | 0
2020-10-21 | 2.9 | 0
2020-10-22 | 2 | 0
2020-10-23 | 1 | 0
2020-10-24 | 6 | 0
2020-10-25 | 22.3 | 0
2020-10-26 | 20.2 | 0
2020-10-27 | 14.9 | 0
2020-10-28 | 18.8 | 0
2020-10-29 | 20.8 | 0
2020-10-30 | 31.1 | 0
2020-10-31 | 35.2 | 0
2020-11-01 | 25.5 | 0
2020-11-02 | 28.5 | 0
2020-11-03 | 28.1 | 0
2020-11-04 | 21.7 | 0
2020-11-05 | 9.5 | 0
2020-11-06 | 10.3 | 0
2020-11-07 | 11.5 | 0
2020-11-08 | 14.2 | 0
2020-11-09 | 16.2 | 0
2020-11-10 | 11.4 | 0
2020-11-11 | 3.1 | 0
2020-11-12 | 11.9 | 0
2020-11-13 | 24.2 | 0
2020-11-14 | 26.4 | 0
2020-11-15 | 26 | 0
2020-11-16 | 20.5 | 0
2020-11-17 | 29.5 | 0
2020-11-18 | 37.1 | 0
2020-11-19 | 33 | 0
2020-11-20 | 14.2 | 0
2020-11-21 | 19.2 | 0
2020-11-22 | 28.2 | 0
2020-11-23 | 24.6 | 0
2020-11-24 | 29.7 | 0
2020-11-25 | 29.1 | 0
2020-11-26 | 23.2 | 0
2020-11-27 | 19.9 | 0
2020-11-28 | 21 | 0
2020-11-29 | 27.4 | 0
2020-11-30 | 19.6 | 0
2020-12-01 | 12.1 | 0
2020-12-02 | 27.6 | 0
2020-12-03 | 25.5 | 0
2020-12-04 | 18.4 | 0
2020-12-05 | 25.8 | 0
2020-12-06 | 32.3 | 0
2020-12-07 | 34.1 | 0
2020-12-08 | 36.7 | 0
2020-12-09 | 35.2 | 0
2020-12-10 | 28.4 | 0
2020-12-11 | 29 | 0
2020-12-12 | 27.2 | 0
2020-12-13 | 20.6 | 0
2020-12-14 | 31.8 | 0
2020-12-15 | 34.5 | 0
2020-12-16 | 44.4 | 0
2020-12-17 | 42.8 | 0
2020-12-18 | 43.5 | 0
2020-12-19 | 51.1 | 0
2020-12-20 | 40.1 | 0
2020-12-21 | 33 | 0
2020-12-22 | 30.9 | 0
2020-12-23 | 32.9 | 2
2020-12-24 | 23 | 0
2020-12-25 | 12 | 0
2020-12-26 | 35.8 | 0
2020-12-27 | 37.1 | 0
2020-12-28 | 30.6 | 0
2020-12-29 | 33.9 | 0
2020-12-30 | 36.4 | 0
2020-12-31 | 27.8 | 0
2021-01-01 | 35.5 | 0
2021-01-02 | 30.2 | 0
2021-01-03 | 35.6 | 0
2021-01-04 | 33.6 | 0
2021-01-05 | 31.1 | 0
2021-01-06 | 31.8 | 0
2021-01-07 | 32.9 | 0
2021-01-08 | 37.1 | 0
2021-01-09 | 37 | 2
2021-01-10 | 36.7 | 5
2021-01-11 | 41.8 | 0
2021-01-12 | 37.2 | 0
2021-01-13 | 33.2 | 0
2021-01-14 | 33.3 | 0
2021-01-15 | 30.9 | 0
2021-01-16 | 27.9 | 0
2021-01-17 | 28 | 0
2021-01-18 | 28.4 | 0
2021-01-19 | 34.3 | 0
2021-01-20 | 36.9 | 0
2021-01-21 | 39.3 | 0
2021-01-22 | 33 | 0
2021-01-23 | 41.7 | 0
2021-01-24 | 45.7 | 0
2021-01-25 | 40.3 | 1
2021-01-26 | 39.3 | 0
2021-01-27 | 35.7 | 0
2021-01-28 | 40.9 | 0
2021-01-29 | 53.8 | 0
2021-01-30 | 53 | 0
2021-01-31 | 54.4 | 0
2021-02-01 | 42.6 | 0
2021-02-02 | 33.2 | 0
2021-02-03 | 34.2 | 0
2021-02-04 | 35.2 | 0
2021-02-05 | 38.1 | 0
2021-02-06 | 36.3 | 0
2021-02-07 | 41.6 | 0
2021-02-08 | 45.6 | 0
2021-02-09 | 44.7 | 0
2021-02-10 | 44.9 | 0
2021-02-11 | 42.7 | 0
2021-02-12 | 47.7 | 0
2021-02-13 | 43.5 | 0
2021-02-14 | 35.9 | 0
2021-02-15 | 36.3 | 0
2021-02-16 | 31.4 | 0
2021-02-17 | 41 | 0
2021-02-18 | 41.1 | 0
2021-02-19 | 38.4 | 0
2021-02-20 | 38.1 | 0
2021-02-21 | 43.4 | 0
2021-02-22 | 39.1 | 0
2021-02-23 | 28.9 | 0
2021-02-24 | 22.7 | 0
2021-02-25 | 26.4 | 0
2021-02-26 | 33 | 0
2021-02-27 | 32.1 | 0
2021-02-28 | 28.7 | 0
2021-03-01 | 30.1 | 0
2021-03-02 | 45.2 | 0
2021-03-03 | 31.5 | 3
2021-03-04 | 31.7 | 0
2021-03-05 | 39.2 | 0
2021-03-06 | 40.2 | 0
2021-03-07 | 38 | 0
2021-03-08 | 35.4 | 0
2021-03-09 | 24.2 | 0
2021-03-10 | 25.7 | 0
2021-03-11 | 13.3 | 0
2021-03-12 | 11.5 | 0
2021-03-13 | 29.7 | 0
2021-03-14 | 29.7 | 0
2021-03-15 | 41.6 | 0
2021-03-16 | 38.7 | 2
2021-03-17 | 27.5 | 6
2021-03-18 | 24.6 | 5
2021-03-19 | 30.9 | 0
2021-03-20 | 27 | 0
2021-03-21 | 20.9 | 0
2021-03-22 | 20.4 | 1
2021-03-23 | 17.1 | 0
2021-03-24 | 16 | 0
2021-03-25 | 7.8 | 0
2021-03-26 | 7 | 0
2021-03-27 | 12.9 | 0
2021-03-28 | 19.1 | 0
2021-03-29 | 22.1 | 0
2021-03-30 | 21.9 | 0
2021-03-31 | 12.3 | 0
2021-04-01 | 21.7 | 0
2021-04-02 | 34.3 | 0
2021-04-03 | 28.5 | 0
2021-04-04 | 22.4 | 0
2021-04-05 | 12.3 | 0
2021-04-06 | 11.9 | 0
2021-04-07 | 12.2 | 0
2021-04-08 | 10.7 | 0
2021-04-09 | 10.7 | 0
2021-04-10 | 6 | 0
2021-04-11 | 12.5 | 0
2021-04-12 | 17.1 | 0
2021-04-13 | 12.3 | 0
2021-04-14 | 8.8 | 0
2021-04-15 | 19.1 | 0
2021-04-16 | 27.7 | 0
2021-04-17 | 20.3 | 0
2021-04-18 | 14.3 | 0
2021-04-19 | 13.5 | 0
2021-04-20 | 12.3 | 0
2021-04-21 | 18.4 | 0
2021-04-22 | 27.3 | 1
2021-04-23 | 18 | 1
2021-04-24 | 10.7 | 0
2021-04-25 | 13.2 | 0
2021-04-26 | 18 | 0
2021-04-27 | 14 | 0
2021-04-28 | 7.6 | 0
2021-04-29 | 9.7 | 0
2021-04-30 | 11.1 | 0
2021-05-01 | 17.5 | 0
2021-05-02 | 10.2 | 0
2021-05-03 | 7 | 0
2021-05-04 | 11 | 0
2021-05-05 | 13.2 | 0
2021-05-06 | 9.8 | 0
2021-05-07 | 12.1 | 0
2021-05-08 | 13.7 | 0
2021-05-09 | 10.6 | 0
2021-05-10 | 11.7 | 0
2021-05-11 | 10.7 | 0
2021-05-12 | 11.1 | 0
2021-05-13 | 11.1 | 0
2021-05-14 | 9.9 | 0
2021-05-15 | 5.8 | 0
2021-05-16 | 4.2 | 0
2021-05-17 | 6.9 | 0
2021-05-18 | 5.6 | 0
2021-05-19 | 3.9 | 0
2021-05-20 | 4.1 | 0
2021-05-21 | 3.8 | 0
2021-05-22 | 2 | 0
2021-05-23 | 0.5 | 0
2021-05-24 | 6.5 | 0
2021-05-25 | 5.3 | 0
2021-05-26 | 1.7 | 0
2021-05-27 | 0.4 | 0
2021-05-28 | 11.5 | 0
2021-05-29 | 19.4 | 0
2021-05-30 | 17.4 | 0
2021-05-31 | 11.3 | 0
2021-06-01 | 7.9 | 0
2021-06-02 | 4.8 | 0
2021-06-03 | 2.4 | 0
2021-06-04 | 0.1 | 0
2021-06-05 | 1.7 | 0
2021-06-06 | 0.4 | 1
2021-06-07 | 0.1 | 0
2021-06-08 | 0 | 0
2021-06-09 | 0 | 0
2021-06-10 | 0.7 | 0
2021-06-11 | 3.4 | 0
2021-06-12 | 3 | 0
2021-06-13 | 2.5 | 0
2021-06-14 | 2.4 | 0
2021-06-15 | 0.4 | 0
2021-06-16 | 1.9 | 0
2021-06-17 | 5.7 | 0
2021-06-18 | 5.1 | 0
2021-06-19 | 0 | 0
2021-06-20 | 0 | 0
2021-06-21 | 0 | 0
2021-06-22 | 1.7 | 0
2021-06-23 | 5.1 | 0
2021-06-24 | 5.9 | 0
2021-06-25 | 2.2 | 0
2021-06-26 | 0 | 0
2021-06-27 | 0 | 0
2021-06-28 | 0 | 0
2021-06-29 | 0 | 0
2021-06-30 | 0 | 0
2021-07-01 | 0 | 0
2021-07-02 | 2.5 | 0
2021-07-03 | 6.2 | 0
2021-07-04 | 3.7 | 0
2021-07-05 | 1.6 | 0
2021-07-06 | 0 | 0
2021-07-07 | 0 | 0
2021-07-08 | 0 | 0
2021-07-09 | 0 | 0
2021-07-10 | 0 | 0
2021-07-11 | 0 | 0
2021-07-12 | 0.6 | 0
2021-07-13 | 0 | 0
2021-07-14 | 0 | 0
2021-07-15 | 0 | 0
2021-07-16 | 0 | 0
2021-07-17 | 0 | 0
2021-07-18 | 0 | 0
2021-07-19 | 0 | 0
2021-07-20 | 0.1 | 0
2021-07-21 | 0 | 0
2021-07-22 | 0.7 | 0
2021-07-23 | 1 | 0
2021-07-24 | 2.1 | 0
2021-07-25 | 0 | 0
2021-07-26 | 0 | 0
2021-07-27 | 1.1 | 0
2021-07-28 | 0.3 | 0
2021-07-29 | 0.8 | 0
2021-07-30 | 0.6 | 0
2021-07-31 | 4.7 | 0
2021-08-01 | 4.2 | 0
2021-08-02 | 0.8 | 0
2021-08-03 | 3.9 | 0
2021-08-04 | 2.4 | 0
2021-08-05 | 0.1 | 0
2021-08-06 | 0.4 | 0
2021-08-07 | 0.1 | 0
2021-08-08 | 0 | 0
2021-08-09 | 0 | 0
2021-08-10 | 0 | 0
2021-08-11 | 0 | 0
2021-08-12 | 0 | 0
2021-08-13 | 0 | 0
2021-08-14 | 0 | 0
2021-08-15 | 1.5 | 0
2021-08-16 | 2.1 | 0
2021-08-17 | 1.3 | 0
2021-08-18 | 0 | 0
2021-08-19 | 0 | 0
2021-08-20 | 0 | 0
2021-08-21 | 0 | 0
2021-08-22 | 0 | 0
2021-08-23 | 0 | 0
2021-08-24 | 0 | 0
2021-08-25 | 0 | 0
2021-08-26 | 0 | 0
2021-08-27 | 0 | 0
2021-08-28 | 0.1 | 0
2021-08-29 | 0.8 | 0
2021-08-30 | 0 | 0
2021-08-31 | 0.2 | 0
2021-09-01 | 1.2 | 0
2021-09-02 | 3.2 | 2
2021-09-03 | 5.4 | 0
2021-09-04 | 5.1 | 0
2021-09-05 | 3.1 | 0
2021-09-06 | 0.6 | 0
2021-09-07 | 4.5 | 0
2021-09-08 | 2.5 | 0
2021-09-09 | 0 | 0
2021-09-10 | 1.8 | 0
2021-09-11 | 6.5 | 0
2021-09-12 | 1.7 | 0
2021-09-13 | 0.7 | 0
2021-09-14 | 2.5 | 0
2021-09-15 | 0 | 0
2021-09-16 | 0.1 | 0
2021-09-17 | 0 | 1
2021-09-18 | 0 | 0
2021-09-19 | 3.3 | 0
2021-09-20 | 5.7 | 0
2021-09-21 | 5.2 | 0
2021-09-22 | 0.6 | 0
2021-09-23 | 0 | 0
2021-09-24 | 2 | 0
2021-09-25 | 6.7 | 0
2021-09-26 | 4.6 | 0
2021-09-27 | 5.8 | 0
2021-09-28 | 2.9 | 0
2021-09-29 | 9.7 | 0
2021-09-30 | 11.2 | 0
2021-10-01 | 12.8 | 0
2021-10-02 | 8.7 | 0
2021-10-03 | 4.3 | 0
2021-10-04 | 7.1 | 0
2021-10-05 | 9.1 | 0
2021-10-06 | 5.9 | 0
2021-10-07 | 6.9 | 1
2021-10-08 | 5.1 | 0
2021-10-09 | 5.7 | 0
2021-10-10 | 6.5 | 0
2021-10-11 | 4.9 | 0
2021-10-12 | 7.7 | 0
2021-10-13 | 7.9 | 0
2021-10-14 | 4.5 | 0
2021-10-15 | 3.6 | 0
2021-10-16 | 1.2 | 0
2021-10-17 | 9.7 | 0
2021-10-18 | 15.4 | 0
2021-10-19 | 14.4 | 0
2021-10-20 | 5.5 | 0
2021-10-21 | 6.3 | 0
2021-10-22 | 6.1 | 0
2021-10-23 | 15.6 | 0
2021-10-24 | 17.8 | 0
2021-10-25 | 15.7 | 0
2021-10-26 | 14.5 | 0
2021-10-27 | 12.1 | 0
2021-10-28 | 17.7 | 0
2021-10-29 | 22 | 0
2021-10-30 | 12.9 | 0
2021-10-31 | 7.6 | 0
2021-11-01 | 15.1 | 0
2021-11-02 | 19.6 | 0
2021-11-03 | 25.8 | 0
2021-11-04 | 28.6 | 0
2021-11-05 | 28.7 | 0
2021-11-06 | 30.2 | 0
2021-11-07 | 30.2 | 0
2021-11-08 | 21 | 0
2021-11-09 | 15.9 | 0
2021-11-10 | 13 | 0
2021-11-11 | 21.1 | 0
2021-11-12 | 14.4 | 0
2021-11-13 | 23.7 | 2
2021-11-14 | 23.6 | 6
2021-11-15 | 24.9 | 0
2021-11-16 | 26.1 | 0
2021-11-17 | 25.7 | 0
2021-11-18 | 10.6 | 0
2021-11-19 | 24.9 | 0
2021-11-20 | 31.3 | 0
2021-11-21 | 22.3 | 0
2021-11-22 | 21.3 | 0
2021-11-23 | 33.1 | 0
2021-11-24 | 34.1 | 0
2021-11-25 | 30 | 0
2021-11-26 | 27 | 0
2021-11-27 | 32.4 | 0
2021-11-28 | 33.8 | 0
2021-11-29 | 32.7 | 0
2021-11-30 | 35.6 | 0
2021-12-01 | 30.1 | 0
2021-12-02 | 22.5 | 0
2021-12-03 | 28 | 0
2021-12-04 | 33.6 | 0
2021-12-05 | 30.5 | 0
2021-12-06 | 21.8 | 0
2021-12-07 | 30.5 | 1
2021-12-08 | 35 | 0
2021-12-09 | 36 | 0
2021-12-10 | 33.6 | 0
2021-12-11 | 25.7 | 0
2021-12-12 | 25.4 | 0
2021-12-13 | 25.3 | 0
2021-12-14 | 25.9 | 0
2021-12-15 | 31.3 | 0
2021-12-16 | 13.7 | 0
2021-12-17 | 13.6 | 0
2021-12-18 | 29.9 | 0
2021-12-19 | 33.8 | 0
2021-12-20 | 40.9 | 0
2021-12-21 | 35 | 0
2021-12-22 | 30.9 | 0
2021-12-23 | 38.5 | 0
2021-12-24 | 41.4 | 0
2021-12-25 | 35 | 0
2021-12-26 | 27.5 | 0
2021-12-27 | 34.1 | 0
2021-12-28 | 29.7 | 0
2021-12-29 | 29.3 | 0
2021-12-30 | 25.2 | 0
2021-12-31 | 21.6 | 0
2022-01-01 | 17.3 | 0
2022-01-02 | 22.7 | 0
2022-01-03 | 40.6 | 0
2022-01-04 | 42.3 | 0
2022-01-05 | 34 | 0
2022-01-06 | 34.5 | 0
2022-01-07 | 38.6 | 0
2022-01-08 | 47.6 | 0
2022-01-09 | 35.3 | 0
2022-01-10 | 40.3 | 0
2022-01-11 | 55.5 | 0
2022-01-12 | 43.3 | 0
2022-01-13 | 33.8 | 0
2022-01-14 | 36.4 | 0
2022-01-15 | 57.7 | 0
2022-01-16 | 54 | 0
2022-01-17 | 31.1 | 0
2022-01-18 | 40.3 | 0
2022-01-19 | 35.9 | 0
2022-01-20 | 35.3 | 0
2022-01-21 | 53.2 | 0
2022-01-22 | 52.2 | 0
2022-01-23 | 41.4 | 0
2022-01-24 | 41.5 | 0
2022-01-25 | 36 | 0
2022-01-26 | 49 | 0
2022-01-27 | 51.7 | 0
2022-01-28 | 37.3 | 0
2022-01-29 | 48.8 | 0
2022-01-30 | 54.2 | 0
2022-01-31 | 52.7 | 2
2022-02-01 | 43.8 | 12
2022-02-02 | 31.4 | 0
2022-02-03 | 25.2 | 0
2022-02-04 | 33.2 | 0
2022-02-05 | 45.9 | 0
2022-02-06 | 48.3 | 0
2022-02-07 | 39.2 | 0
2022-02-08 | 30.1 | 0
2022-02-09 | 32.4 | 0
2022-02-10 | 29.3 | 0
2022-02-11 | 26.8 | 0
2022-02-12 | 21.6 | 0
2022-02-13 | 36.9 | 0
2022-02-14 | 48.2 | 0
2022-02-15 | 46.3 | 0
2022-02-16 | 37.4 | 0
2022-02-17 | 13.2 | 0
2022-02-18 | 26.8 | 0
2022-02-19 | 42.6 | 0
2022-02-20 | 41.8 | 0
2022-02-21 | 27.5 | 0
2022-02-22 | 28.5 | 0
2022-02-23 | 16.2 | 0
2022-02-24 | 39 | 0
2022-02-25 | 40.9 | 0
2022-02-26 | 43.9 | 0
2022-02-27 | 38.9 | 0
2022-02-28 | 44 | 0
2022-03-01 | 38.6 | 0
2022-03-02 | 30.2 | 0
2022-03-03 | 35.4 | 0
2022-03-04 | 42.7 | 0
2022-03-05 | 36.9 | 0
2022-03-06 | 16 | 0
2022-03-07 | 16.5 | 0
2022-03-08 | 28.9 | 0
2022-03-09 | 35.8 | 0
2022-03-10 | 32.1 | 0
2022-03-11 | 26.2 | 0
2022-03-12 | 33.4 | 0
2022-03-13 | 36.9 | 0
2022-03-14 | 27.3 | 0
2022-03-15 | 18 | 0
2022-03-16 | 19.2 | 0
2022-03-17 | 20.9 | 0
2022-03-18 | 10.6 | 0
2022-03-19 | 14 | 0
2022-03-20 | 16 | 0
2022-03-21 | 17.2 | 0
2022-03-22 | 22.1 | 0
2022-03-23 | 27.2 | 0
2022-03-24 | 26.7 | 0
2022-03-25 | 16.6 | 0
2022-03-26 | 20.6 | 0
2022-03-27 | 26.7 | 0
2022-03-28 | 41.2 | 0
2022-03-29 | 38 | 0
2022-03-30 | 28.7 | 0
2022-03-31 | 17.8 | 0
2022-04-01 | 16.8 | 0
2022-04-02 | 23.2 | 0
2022-04-03 | 26 | 0
2022-04-04 | 20 | 0
2022-04-05 | 18.7 | 0
2022-04-06 | 20 | 0
2022-04-07 | 18.2 | 0
2022-04-08 | 15 | 0
2022-04-09 | 21.6 | 0
2022-04-10 | 22.5 | 0
2022-04-11 | 16.4 | 0
2022-04-12 | 10.6 | 0
2022-04-13 | 8.3 | 0
2022-04-14 | 7.2 | 0
2022-04-15 | 9.5 | 0
2022-04-16 | 11.7 | 0
2022-04-17 | 23.6 | 0
2022-04-18 | 22 | 0
2022-04-19 | 21.7 | 0
2022-04-20 | 19.5 | 0
2022-04-21 | 19.5 | 0
2022-04-22 | 12.9 | 0
2022-04-23 | 14.7 | 0
2022-04-24 | 13.3 | 0
2022-04-25 | 12.1 | 0
2022-04-26 | 13.8 | 0
2022-04-27 | 17 | 0
2022-04-28 | 19.9 | 0
2022-04-29 | 17.3 | 0
2022-04-30 | 16.2 | 0
2022-05-01 | 12.4 | 0
2022-05-02 | 13.9 | 0
2022-05-03 | 14.1 | 0
2022-05-04 | 14 | 0
2022-05-05 | 9.5 | 1
2022-05-06 | 9.5 | 0
2022-05-07 | 14 | 0
2022-05-08 | 14.7 | 0
2022-05-09 | 11.8 | 0
2022-05-10 | 8.9 | 0
2022-05-11 | 7.5 | 0
2022-05-12 | 4.1 | 0
2022-05-13 | 1.1 | 0
2022-05-14 | 0 | 0
2022-05-15 | 0.4 | 0
2022-05-16 | 1.3 | 0
2022-05-17 | 4.4 | 0
2022-05-18 | 5.8 | 0
2022-05-19 | 10.6 | 0
2022-05-20 | 7 | 0
2022-05-21 | 0.9 | 0
2022-05-22 | 0 | 0
2022-05-23 | 2.2 | 0
2022-05-24 | 5.2 | 0
2022-05-25 | 7.1 | 0
2022-05-26 | 5.4 | 0
2022-05-27 | 0.6 | 0
2022-05-28 | 0.7 | 0
2022-05-29 | 4.3 | 0
2022-05-30 | 3.3 | 0
2022-05-31 | 0.2 | 0
2022-06-01 | 3.8 | 0
2022-06-02 | 3.4 | 0
2022-06-03 | 1.5 | 0
2022-06-04 | 1.6 | 0
2022-06-05 | 4.9 | 0
2022-06-06 | 4.7 | 0
2022-06-07 | 1.9 | 0
2022-06-08 | 0.8 | 0
2022-06-09 | 2.2 | 0
2022-06-10 | 2.5 | 0
2022-06-11 | 5.2 | 0
2022-06-12 | 3.7 | 0
2022-06-13 | 0.1 | 0
2022-06-14 | 2 | 0
2022-06-15 | 2.3 | 0
2022-06-16 | 0.4 | 0
2022-06-17 | 0 | 0
2022-06-18 | 3.7 | 0
2022-06-19 | 5.7 | 0
2022-06-20 | 3.5 | 0
2022-06-21 | 4 | 0
2022-06-22 | 5.2 | 0
2022-06-23 | 2.8 | 0
2022-06-24 | 1.4 | 0
2022-06-25 | 0.9 | 0
2022-06-26 | 0.6 | 0
2022-06-27 | 0 | 0
2022-06-28 | 2.6 | 0
2022-06-29 | 3.4 | 0
2022-06-30 | 1.9 | 1
2022-07-01 | 0.8 | 7
2022-07-02 | 0 | 0
2022-07-03 | 0.4 | 0
2022-07-04 | 1.7 | 0
2022-07-05 | 1 | 0
2022-07-06 | 0.2 | 0
2022-07-07 | 2 | 0
2022-07-08 | 0.6 | 0
2022-07-09 | 0.8 | 0
2022-07-10 | 3.8 | 0
2022-07-11 | 2.5 | 0
2022-07-12 | 0 | 0
2022-07-13 | 0.1 | 0
2022-07-14 | 0.1 | 0
2022-07-15 | 1.9 | 0
2022-07-16 | 2.1 | 0
2022-07-17 | 0.2 | 0
2022-07-18 | 0 | 0
2022-07-19 | 0 | 0
2022-07-20 | 0 | 0
2022-07-21 | 0 | 0
2022-07-22 | 0 | 0
2022-07-23 | 0 | 0
2022-07-24 | 0 | 0
2022-07-25 | 0 | 0
2022-07-26 | 0.5 | 0
2022-07-27 | 2.5 | 0
2022-07-28 | 0.2 | 0
2022-07-29 | 0 | 0
2022-07-30 | 0.1 | 0
2022-07-31 | 1.1 | 0
2022-08-01 | 0 | 0
2022-08-02 | 0 | 0
2022-08-03 | 0.2 | 0
2022-08-04 | 0.1 | 0
2022-08-05 | 0 | 0
2022-08-06 | 0 | 0
2022-08-07 | 0 | 0
2022-08-08 | 0 | 0
2022-08-09 | 0 | 0
2022-08-10 | 0 | 0
2022-08-11 | 0.3 | 0
2022-08-12 | 0.8 | 0
2022-08-13 | 4.2 | 0
2022-08-14 | 3.8 | 1
2022-08-15 | 2.8 | 1
2022-08-16 | 2.3 | 0
2022-08-17 | 0 | 0
2022-08-18 | 0.6 | 0
2022-08-19 | 1.7 | 0
2022-08-20 | 0.3 | 0
2022-08-21 | 0.1 | 0
2022-08-22 | 0 | 0
2022-08-23 | 0 | 0
2022-08-24 | 0 | 0
2022-08-25 | 0.1 | 0
2022-08-26 | 0 | 0
2022-08-27 | 0.1 | 0
2022-08-28 | 0.5 | 0
2022-08-29 | 0 | 0
2022-08-30 | 0 | 0
2022-08-31 | 0.6 | 0
2022-09-01 | 3 | 0
2022-09-02 | 6.2 | 0
2022-09-03 | 4.4 | 0
2022-09-04 | 1.3 | 0
2022-09-05 | 0.1 | 0
2022-09-06 | 1.8 | 0
2022-09-07 | 1.4 | 0
2022-09-08 | 3.3 | 0
2022-09-09 | 4.9 | 0
2022-09-10 | 3.2 | 0
2022-09-11 | 0.9 | 0
2022-09-12 | 0.3 | 0
2022-09-13 | 0 | 0
2022-09-14 | 2.8 | 0
2022-09-15 | 3.8 | 0
2022-09-16 | 9.2 | 0
2022-09-17 | 7.5 | 0
2022-09-18 | 3 | 0
2022-09-19 | 0.3 | 0
2022-09-20 | 1.8 | 0
2022-09-21 | 3.2 | 0
2022-09-22 | 2.6 | 0
2022-09-23 | 11.5 | 0
2022-09-24 | 11.3 | 0
2022-09-25 | 9.9 | 0
2022-09-26 | 5.2 | 0
2022-09-27 | 8.5 | 0
2022-09-28 | 8 | 0
2022-09-29 | 10.1 | 0
2022-09-30 | 14.8 | 0
2022-10-01 | 10.8 | 0
2022-10-02 | 11.7 | 0
2022-10-03 | 15.5 | 0
2022-10-04 | 14.2 | 0
2022-10-05 | 9.5 | 0
2022-10-06 | 6.1 | 0
2022-10-07 | 7.3 | 0
2022-10-08 | 16.2 | 0
2022-10-09 | 18.5 | 0
2022-10-10 | 13.7 | 0
2022-10-11 | 15.3 | 0
2022-10-12 | 11.6 | 0
2022-10-13 | 5.8 | 0
2022-10-14 | 9.3 | 0
2022-10-15 | 14.8 | 0
2022-10-16 | 13.5 | 0
2022-10-17 | 18.1 | 0
2022-10-18 | 15.5 | 0
2022-10-19 | 23.6 | 0
2022-10-20 | 21.6 | 0
2022-10-21 | 21.8 | 0
2022-10-22 | 18.3 | 0
2022-10-23 | 16.6 | 0
2022-10-24 | 10 | 0
2022-10-25 | 4.4 | 0
2022-10-26 | 1.4 | 0
2022-10-27 | 8.1 | 0
2022-10-28 | 21 | 0
2022-10-29 | 22.8 | 0
2022-10-30 | 22.8 | 0
2022-10-31 | 15.2 | 0
2022-11-01 | 7.1 | 0
2022-11-02 | 9.3 | 0
2022-11-03 | 15.4 | 0
2022-11-04 | 12.7 | 0
2022-11-05 | 4.9 | 0
2022-11-06 | 0.4 | 0
2022-11-07 | 2.8 | 0
2022-11-08 | 18.6 | 0
2022-11-09 | 27.5 | 0
2022-11-10 | 15.3 | 0
2022-11-11 | 8.9 | 0
2022-11-12 | 4 | 0
2022-11-13 | 18.6 | 0
2022-11-14 | 29.4 | 0
2022-11-15 | 34 | 0
2022-11-16 | 27.7 | 0
2022-11-17 | 29.7 | 0
2022-11-18 | 32.8 | 0
2022-11-19 | 35.4 | 1
2022-11-20 | 36.9 | 3
2022-11-21 | 35.2 | 0
2022-11-22 | 30.9 | 0
2022-11-23 | 31.9 | 0
2022-11-24 | 32.1 | 0
2022-11-25 | 23 | 0
2022-11-26 | 23.5 | 0
2022-11-27 | 26.8 | 0
2022-11-28 | 20.7 | 0
2022-11-29 | 33.4 | 0
2022-11-30 | 26.5 | 0
2022-12-01 | 28.6 | 0
2022-12-02 | 31.5 | 0
2022-12-03 | 19.5 | 0
2022-12-04 | 31 | 0
2022-12-05 | 35.2 | 0
2022-12-06 | 27.3 | 0
2022-12-07 | 11.6 | 0
2022-12-08 | 21 | 0
2022-12-09 | 31.3 | 0
2022-12-10 | 33.6 | 0
2022-12-11 | 37.3 | 0
2022-12-12 | 38.8 | 0
2022-12-13 | 41.7 | 1
2022-12-14 | 36.1 | 0
2022-12-15 | 32.8 | 0
2022-12-16 | 30.9 | 0
2022-12-17 | 29.1 | 0
2022-12-18 | 33.6 | 0
2022-12-19 | 32.6 | 0
2022-12-20 | 34.7 | 0
2022-12-21 | 40.2 | 0
2022-12-22 | 36.3 | 0
2022-12-23 | 25 | 0
2022-12-24 | 55.5 | 0
2022-12-25 | 48.5 | 0
2022-12-26 | 43 | 0
2022-12-27 | 39.4 | 0
2022-12-28 | 35.6 | 1
2022-12-29 | 31.8 | 0
2022-12-30 | 22.3 | 0
2022-12-31 | 23.3 | 0
2023-01-01 | 23.9 | 0
2023-01-02 | 31.3 | 0
2023-01-03 | 31.2 | 0
2023-01-04 | 24.9 | 0
2023-01-05 | 24.1 | 0
2023-01-06 | 31.3 | 0
2023-01-07 | 29.7 | 0
2023-01-08 | 36.8 | 0
2023-01-09 | 34.7 | 0
2023-01-10 | 30.2 | 0
2023-01-11 | 38.6 | 0
2023-01-12 | 34.4 | 0
2023-01-13 | 24.9 | 0
2023-01-14 | 33.4 | 0
2023-01-15 | 32.3 | 0
2023-01-16 | 33.6 | 0
2023-01-17 | 30.1 | 0
2023-01-18 | 24.5 | 0
2023-01-19 | 30.6 | 0
2023-01-20 | 30.1 | 0
2023-01-21 | 32.2 | 0
2023-01-22 | 32.7 | 0
2023-01-23 | 32.4 | 0
2023-01-24 | 30.5 | 0
2023-01-25 | 33.9 | 0
2023-01-26 | 27.8 | 0
2023-01-27 | 33.7 | 0
2023-01-28 | 29.4 | 0
2023-01-29 | 27.7 | 0
2023-01-30 | 26.4 | 0
2023-01-31 | 33.8 | 0
2023-02-01 | 40.8 | 0
2023-02-02 | 39.3 | 0
2023-02-03 | 52.3 | 0
2023-02-04 | 62.6 | 0
2023-02-05 | 33.5 | 0
2023-02-06 | 31.1 | 0
2023-02-07 | 35.5 | 0
2023-02-08 | 29.3 | 0
2023-02-09 | 33 | 0
2023-02-10 | 22.3 | 0
2023-02-11 | 30.5 | 0
2023-02-12 | 33.5 | 0
2023-02-13 | 27.6 | 0
2023-02-14 | 24 | 0
2023-02-15 | 21 | 0
2023-02-16 | 17.7 | 0
2023-02-17 | 23 | 0
2023-02-18 | 35.7 | 0
2023-02-19 | 29.9 | 0
2023-02-20 | 20.9 | 0
2023-02-21 | 30 | 0
2023-02-22 | 31.1 | 0
2023-02-23 | 35.4 | 0
2023-02-24 | 37.3 | 0

## full_electric_billing_data
TYPE | START DATE | END DATE | USAGE | UNITS | COST | days | daily use | Winter seasonal avg
Electric billing | 2018-08-18 | 2018-08-21 | 93 | kWh | 20.34 | 3 | 31
Electric billing | 2018-08-22 | 2018-09-21 | 378 | kWh | 82.67 | 30 | 12.6
Electric billing | 2018-09-22 | 2018-10-22 | 286 | kWh | 62.58 | 30 | 9.5333
Electric billing | 2018-10-23 | 2018-11-27 | 416 | kWh | 99.95 | 35 | 11.8857
Electric billing | 2018-11-28 | 2018-12-20 | 248 | kWh | 61.34 | 22 | 11.2727
Electric billing | 2018-12-21 | 2019-01-23 | 442 | kWh | 109.81 | 33 | 13.3939
Electric billing | 2019-01-24 | 2019-02-21 | 402 | kWh | 100.05 | 28 | 14.3571
Electric billing | 2019-02-22 | 2019-03-22 | 312 | kWh | 78.72 | 28 | 11.1429
Electric billing | 2019-03-23 | 2019-04-24 | 366 | kWh | 92.75 | 32 | 11.4375
Electric billing | 2019-04-25 | 2019-05-23 | 356 | kWh | 81.46 | 28 | 12.7143
Electric billing | 2019-05-24 | 2019-06-21 | 285 | kWh | 63.95 | 28 | 10.1786
Electric billing | 2019-06-22 | 2019-07-24 | 223 | kWh | 50.05 | 32 | 6.9688
Electric billing | 2019-07-25 | 2019-08-26 | 318 | kWh | 71.35 | 32 | 9.9375
Electric billing | 2019-08-27 | 2019-09-23 | 365 | kWh | 81.87 | 27 | 13.5185
Electric billing | 2019-09-24 | 2019-10-24 | 483 | kWh | 108.36 | 30 | 16.1
Electric billing | 2019-10-25 | 2019-11-20 | 446 | kWh | 110.98 | 26 | 17.1538
Electric billing | 2019-11-21 | 2019-12-20 | 463 | kWh | 119.14 | 29 | 15.9655
Electric billing | 2019-12-21 | 2020-01-23 | 503 | kWh | 130.15 | 33 | 15.2424
Electric billing | 2020-01-24 | 2020-02-21 | 494 | kWh | 128.17 | 28 | 17.6429 | 15.7262
Electric billing | 2020-02-22 | 2020-03-24 | 384 | kWh | 101.58 | 31 | 12.3871
Electric billing | 2020-03-25 | 2020-04-23 | 463 | kWh | 123.25 | 29 | 15.9655
Electric billing | 2020-04-24 | 2020-05-21 | 365 | kWh | 86.9 | 27 | 13.5185
Electric billing | 2020-05-22 | 2020-06-23 | 596 | kWh | 136.29 | 32 | 18.625
Electric billing | 2020-06-24 | 2020-07-23 | 636 | kWh | 145.5 | 29 | 21.931
Electric billing | 2020-07-24 | 2020-08-21 | 659 | kWh | 147.35 | 28 | 23.5357
Electric billing | 2020-08-22 | 2020-09-21 | 482 | kWh | 106.82 | 30 | 16.0667
Electric billing | 2020-09-22 | 2020-10-21 | 414 | kWh | 91.5 | 29 | 14.2759
Electric billing | 2020-10-22 | 2020-11-19 | 448 | kWh | 106.28 | 28 | 16
Electric billing | 2020-11-20 | 2020-12-22 | 470 | kWh | 115.6 | 32 | 14.6875
Electric billing | 2020-12-23 | 2021-01-22 | 505 | kWh | 126.59 | 30 | 16.8333
Electric billing | 2021-01-23 | 2021-02-24 | 480 | kWh | 121.27 | 32 | 15 | 14.8904
Electric billing | 2021-02-25 | 2021-03-25 | 358 | kWh | 94.28 | 28 | 12.7857
Electric billing | 2021-03-26 | 2021-04-23 | 393 | kWh | 104.15 | 28 | 14.0357
Electric billing | 2021-04-24 | 2021-05-21 | 409 | kWh | 97.94 | 27 | 15.1481
Electric billing | 2021-05-22 | 2021-06-23 | 752 | kWh | 175.77 | 32 | 23.5
Electric billing | 2021-06-24 | 2021-07-23 | 648 | kWh | 152.48 | 29 | 22.3448
Electric billing | 2021-07-24 | 2021-08-25 | 564 | kWh | 132.77 | 32 | 17.625
Electric billing | 2021-08-26 | 2021-09-22 | 649 | kWh | 152.79 | 27 | 24.037
Electric billing | 2021-09-23 | 2021-10-25 | 642 | kWh | 151.18 | 32 | 20.0625
Electric billing | 2021-10-26 | 2021-11-23 | 487 | kWh | 134.5 | 28 | 17.3929
Electric billing | 2021-11-24 | 2021-12-21 | 519 | kWh | 148.91 | 27 | 19.2222
Electric billing | 2021-12-22 | 2022-01-24 | 648 | kWh | 186.27 | 33 | 19.6364
Electric billing | 2022-01-25 | 2022-02-18 | 476 | kWh | 136.92 | 24 | 19.8333 | 18.4496
Electric billing | 2022-02-19 | 2022-03-22 | 577 | kWh | 164.11 | 31 | 18.6129
Electric billing | 2022-03-23 | 2022-04-22 | 480 | kWh | 135.78 | 30 | 16
Electric billing | 2022-04-23 | 2022-05-24 | 637 | kWh | 162.21 | 31 | 20.5484
Electric billing | 2022-05-25 | 2022-06-22 | 688 | kWh | 173.94 | 28 | 24.5714
Electric billing | 2022-06-23 | 2022-07-22 | 694 | kWh | 177.2 | 29 | 23.931
Electric billing | 2022-07-23 | 2022-08-23 | 1002 | kWh | 255.88 | 31 | 32.3226
Electric billing | 2022-08-24 | 2022-09-21 | 704 | kWh | 179.77 | 28 | 25.1429
Electric billing | 2022-09-22 | 2022-10-21 | 670 | kWh | 172.56 | 29 | 23.1034
Electric billing | 2022-10-22 | 2022-11-21 | 816 | kWh | 331.33 | 30 | 27.2
Electric billing | 2022-11-22 | 2022-12-21 | 1209 | kWh | 575.87 | 29 | 41.6897
Electric billing | 2022-12-22 | 2023-01-23 | 1346 | kWh | 641.35 | 32 | 42.0625
Electric billing | 2023-01-24 | 2023-02-21 | 1412 | kWh | 672.93 | 28 | 50.4286

## heating_load_calc
Nameplate efficiency of gas furnace |  |  | 0.93
BTUs/therm |  |  | 99976.1
Base temperature |  |  | 65
Design temperature |  |  | 0
TYPE | START DATE | END DATE | BTU_delivered | BTU_to_heat | BTU_load_HDD
Gas bill | 2021-10-15 | 2021-11-12 | 4298972.3 | 3998044.239 | 8659.3984
Gas bill | 2021-11-13 | 2021-12-13 | 9497729.5 | 8832888.435 | 10139.9247
Gas bill | 2021-12-14 | 2022-01-13 | 10997371 | 10227555.03 | 9996.6328
Gas bill | 2022-01-14 | 2022-02-14 | 14396558.4 | 13388799.312 | 10291.1601
Est. heat load based on coldest winter months (BTUs/HDD) |  |  |  |  | 10142.5726
Est. heat load at design temperature |  |  |  |  | 27469.4673